## alarmdefinitions
[13 empty] | Critical | 7
[13 empty] | Major | 6
[13 empty] | Minor | 5
[13 empty] | Warning | 4
[13 empty] | Normal | 3
[13 empty] | Cleared | 2
[13 empty] | Indeterminate | 1
ALARMS - READ | [12 empty] | OpenNMS alarm definitions
Mimic Component | RTU Alarm Name | Alarm Category | Location | Relay Status | Event Type | Severity | Noc Staff Log user message | Hidden Alarm detials from NOC staff Default Moxa Topic - broker | payload | eventlabel | Log msg | Description | Severity | Open NMS UEI | alarmdata
Switch | 0, MainsPowerStatus | Mains Power | YAKU - Japan | N/A | Environmental Alarm | Emergency | Ground Cabin %nodelabel% Mains Power Failed | YAKU001/read/45MR-1601-0@DI00-GSMains/diStatus | {"value":1} | Environmental Alarm: Ground Cabin Mains Power Failed | Environmental Alarm: Ground Cabin %nodelabel% Mains Power Failed | Environmental Alarm: Ground Cabin %nodelabel% Mains Power Failed&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI00-GSMains/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 0, MainsPowerStatus | Mains Power | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Cabin %nodelabel% Mains Power Failed | YAKU001/read/45MR-1601-0@DI00-GSMains/diStatus | {"value":0} | Environmental Alarm: Ground Cabin Mains Power Failed | Environmental Alarm: Ground Cabin %nodelabel% Mains Power Failed | Environmental Alarm: Ground Cabin %nodelabel% Mains Power Failed&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI00-GSMains/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI00-GSMains/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 1, UPS Down | UPS Power | YAKU - Japan | N/A | Environmental Alarm | Alert | Ground Cabin %nodelabel% UPS Down no backup power supply | YAKU001/read/45MR-1601-0@DI01-UPS/diStatus | {"value":1} | Environmental Alarm: Ground Cabin UPS Down no backup power supply | Environmental Alarm: Ground Cabin %nodelabel% UPS Down no backup power supply | Environmental Alarm: Ground Cabin %nodelabel% UPS Down no backup power supply&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Minor | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI01-UPS/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 1, UPS Down | UPS Power | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Cabin %nodelabel% UPS Down no backup power supply | YAKU001/read/45MR-1601-0@DI01-UPS/diStatus | {"value":0} | Environmental Alarm: Ground Cabin UPS Down no backup power supply | Environmental Alarm: Ground Cabin %nodelabel% UPS Down no backup power supply | Environmental Alarm: Ground Cabin %nodelabel% UPS Down no backup power supply&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Minor | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI01-UPS/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI01-UPS/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 2, QBandPSU | Qband PowerSupply | YAKU - Japan | N/A | Payload Alarm | Emergency | Ground Cabin %nodelabel% Qband Power Supply Unit Failed | YAKU001/read/45MR-1601-0@DI02-QBandPSU/diStatus | {"value":1} | Payload Alarm: Ground Cabin Qband Power Supply Unit Failed | Payload Alarm: Ground Cabin %nodelabel% Qband Power Supply Unit Failed | Payload Alarm: Ground Cabin %nodelabel% Qband Power Supply Unit Failed&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI02-QBandPSU/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 2, QBandPSU | Qband PowerSupply | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% Qband Power Supply Unit Failed | YAKU001/read/45MR-1601-0@DI02-QBandPSU/diStatus | {"value":0} | Payload Alarm: Ground Cabin Qband Power Supply Unit Failed | Payload Alarm: Ground Cabin %nodelabel% Qband Power Supply Unit Failed | Payload Alarm: Ground Cabin %nodelabel% Qband Power Supply Unit Failed&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI02-QBandPSU/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI02-QBandPSU/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 3, Q_band_PA_Status | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Emergency | Ground Cabin %nodelabel% QBand Power Amp Failed | YAKU001/read/45MR-1601-0@DI03-QBandPA_Off/diStatus | {"value":1} | Payload Alarm: Ground Cabin QBand Power Amp Failed | Payload Alarm: Ground Cabin %nodelabel% QBand Power Amp Failed | Payload Alarm: Ground Cabin %nodelabel% QBand Power Amp Failed &lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI03-QBandPA_off/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 3, Q_band_PA_Status | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% QBand Power Amp Failed | YAKU001/read/45MR-1601-0@DI03-QBandPA_Off/diStatus | {"value":0} | Payload Alarm: Ground Cabin QBand Power Amp Failed | Payload Alarm: Ground Cabin %nodelabel% QBand Power Amp Failed | Payload Alarm: Ground Cabin %nodelabel% QBand Power Amp Failed &lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI03-QBandPA_off/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI03-QBandPA_off/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 4, RF_input_over_ limit | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Critical | Ground Cabin %nodelabel% Qband Radio Frequency Over Limit | YAKU001/read/45MR-1601-0@DI04-QBandRFOvrL/diStatus | {"value":1} | Payload Alarm: Ground Cabin Qband Radio Frequency Over Limit | Payload Alarm: Ground Cabin %nodelabel% Qband Radio Frequency Over Limit | Payload Alarm: Ground Cabin %nodelabel% Qband Radio Frequency Over Limit&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI04-QBandRFOverLimit/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 4, RF_input_over_ limit | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% Qband Radio Frequency Over Limit | YAKU001/read/45MR-1601-0@DI04-QBandRFOvrL/diStatus | {"value":0} | Payload Alarm: Ground Cabin Qband Radio Frequency Over Limit | Payload Alarm: Ground Cabin %nodelabel% Qband Radio Frequency Over Limit | Payload Alarm: Ground Cabin %nodelabel% Qband Radio Frequency Over Limit&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI04-QBandRFOverLimit/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI04-QBandRFOverLimit/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 5, QBandOverCurrent | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Alert | Ground Cabin %nodelabel% Qband OverCurrent above safe threshold | YAKU001/read/45MR-1601-0@DI05-QBandOverCu/diStatus | {"value":1} | Payload Alarm: Ground Cabin Qband OverCurrent above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband OverCurrent above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband OverCurrent above safe threshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI05-QBandOverCurrent/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 5, QBandOverCurrent | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% Qband OverCurrent above safe threshold | YAKU001/read/45MR-1601-0@DI05-QBandOverCu/diStatus | {"value":0} | Payload Alarm: Ground Cabin Qband OverCurrent above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband OverCurrent above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband OverCurrent above safe threshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI05-QBandOverCurrent/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI05-QBandOverCurrent/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 6, QBandOverTemperature | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Alert | Ground Cabin %nodelabel% Qband Temperature above safe threshold | YAKU001/read/45MR-1601-0@DI06-QBandOverTm/diStatus | {"value":1} | Payload Alarm: Ground Cabin Qband Temperature above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband Temperature above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband Temperature above safe threshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI06-QBandOverTemp/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 6, QBandOverTemperature | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% Qband Temperature above safe threshold | YAKU001/read/45MR-1601-0@DI06-QBandOverTm/diStatus | {"value":0} | Payload Alarm: Ground Cabin Qband Temperature above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband Temperature above safe threshold | Payload Alarm: Ground Cabin %nodelabel% Qband Temperature above safe threshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI06-QBandOverTemp/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI06-QBandOverTemp/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 7, PositionerControllerStatus [ python app on Intel NUC propering FMS web service at sampling intervals if the plane is in service to confirm that Positioner is aligned with Aircraft] | Payload Antenna | YAKU - Japan | N/A | Payload Alarm | Emergency | Ground Cabin %nodelabel% S-Band Ground Station %nodelabel% Antena Positioner Failed | YAKU001/read/45MR-1601-0@DI07-PosCtrlFail/diStatus | {"value":1} | Payload Alarm: Ground Cabin S-Band Ground Station Antena Positioner Failed | Payload Alarm: Ground Cabin %nodelabel% S-Band Ground Station %nodelabel% Antena Positioner Failed | Payload Alarm: Ground Cabin %nodelabel% S-Band Ground Station %nodelabel% Antena Positioner Failed&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI07-PosCtrlFail/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 7, PositionerControllerStatus [ python app on Intel NUC propering FMS web service at sampling intervals if the plane is in service to confirm that Positioner is aligned with Aircraft] | Payload Antenna | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% S-Band Ground Station %nodelabel% Antena Positioner Failed | YAKU001/read/45MR-1601-0@DI07-PosCtrlFail/diStatus | {"value":0} | Payload Alarm: Ground Cabin S-Band Ground Station Antena Positioner Failed | Payload Alarm: Ground Cabin %nodelabel% S-Band Ground Station %nodelabel% Antena Positioner Failed | Payload Alarm: Ground Cabin %nodelabel% S-Band Ground Station %nodelabel% Antena Positioner Failed&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI07-PosCtrlFail/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI07-PosCtrlFail/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 8, VSWRHigh | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Alert | Ground Cabin %nodelabel% VSWHigh above safe threshold | YAKU001/read/45MR-1601-0@DI08-VSWHigh/diStatus | {"value":1} | Payload Alarm: Ground Cabin VSWHigh above safe threshold | Payload Alarm: Ground Cabin %nodelabel% VSWHigh above safe threshold | Payload Alarm: Ground Cabin %nodelabel% VSWHigh above safe threshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI08-VSWHigh/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 8, VSWRHigh | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% VSWHigh above safe threshold | YAKU001/read/45MR-1601-0@DI08-VSWHigh/diStatus | {"value":0} | Payload Alarm: Ground Cabin VSWHigh above safe threshold | Payload Alarm: Ground Cabin %nodelabel% VSWHigh above safe threshold | Payload Alarm: Ground Cabin %nodelabel% VSWHigh above safe threshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI08-VSWHigh/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI08-VSWHigh/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 9, Bay1DoorStatus | Facilities | YAKU - Japan | N/A | Security Alarm | Warning | Ground Cabin %nodelabel% BayDoor Open | YAKU001/read/45MR-1601-0@DI09-BayDoorStat/diStatus | {"value":1} | Security Alarm: Ground Cabin BayDoor Open | Security Alarm: Ground Cabin %nodelabel% BayDoor Open | Security Alarm: Ground Cabin %nodelabel% BayDoor Open&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI09-BayDoorStatus/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 9, Bay1DoorStatus | Facilities | YAKU - Japan | N/A | Security Alarm | Cleared | Ground Cabin %nodelabel% BayDoor Open | YAKU001/read/45MR-1601-0@DI09-BayDoorStat/diStatus | {"value":0} | Security Alarm: Ground Cabin BayDoor Open | Security Alarm: Ground Cabin %nodelabel% BayDoor Open | Security Alarm: Ground Cabin %nodelabel% BayDoor Open&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI09-BayDoorStatus/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI09-BayDoorStatus/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 10, Antenna PSU | Facilities | YAKU - Japan | N/A | Security Alarm | Emergency | Ground Cabin Station %nodelabel% SiteMonitor Down | YAKU001/read/45MR-1601-0@DI10-AntennaPSU/diStatus | {"value":1} | Security Alarm: Ground Cabin Station SiteMonitor Down | Security Alarm: Ground Cabin Station %nodelabel% SiteMonitor Down | Security Alarm: Ground Cabin Station %nodelabel% SiteMonitor Down&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI10-AntennaPSU/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 10, Antenna PSU | Facilities | YAKU - Japan | N/A | Security Alarm | Cleared | Ground Cabin Station %nodelabel% SiteMonitor Down | YAKU001/read/45MR-1601-0@DI10-AntennaPSU/diStatus | {"value":0} | Security Alarm: Ground Cabin Station SiteMonitor Down | Security Alarm: Ground Cabin Station %nodelabel% SiteMonitor Down | Security Alarm: Ground Cabin Station %nodelabel% SiteMonitor Down&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI10-AntennaPSU/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI10-AntennaPSU/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 11, High Cabinet Temp | Facilities | YAKU - Japan | N/A | Security Alarm | Critical | Ground Cabin %nodelabel% High Cabinet Temperature | YAKU001/read/45MR-1601-0@DI11-HighCapTemp/diStatus | {"value":1} | Security Alarm: Ground Cabin High Cabinet Temperature | Security Alarm: Ground Cabin %nodelabel% High Cabinet Temperature | Security Alarm: Ground Cabin %nodelabel% High Cabinet Temperature&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI11-HighCapTemp/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 11, High Cabinet Temp | Facilities | YAKU - Japan | N/A | Security Alarm | Cleared | Ground Cabin %nodelabel% High Cabinet Temperature | YAKU001/read/45MR-1601-0@DI11-HighCapTemp/diStatus | {"value":0} | Security Alarm: Ground Cabin High Cabinet Temperature | Security Alarm: Ground Cabin %nodelabel% High Cabinet Temperature | Security Alarm: Ground Cabin %nodelabel% High Cabinet Temperature&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI11-HighCapTemp/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI11-HighCapTemp/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 12, Smoke Alarm | Environment | YAKU - Japan | N/A | Payload Alarm | Warning | Ground Cabin %nodelabel% Smoke Alarm triggered on | YAKU001/read/45MR-1601-0@DI12-SmokeAlarm/diStatus | {"value":1} | Payload Alarm: Ground Cabin Smoke Alarm triggered on | Payload Alarm: Ground Cabin %nodelabel% Smoke Alarm triggered on | Payload Alarm: Ground Cabin %nodelabel% Smoke Alarm triggered on&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI12-SmokeAlarm/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 12, Smoke Alarm | Environment | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% Smoke Alarm triggered on | YAKU001/read/45MR-1601-0@DI12-SmokeAlarm/diStatus | {"value":0} | Payload Alarm: Ground Cabin Smoke Alarm triggered on | Payload Alarm: Ground Cabin %nodelabel% Smoke Alarm triggered on | Payload Alarm: Ground Cabin %nodelabel% Smoke Alarm triggered on&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI12-SmokeAlarm/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI12-SmokeAlarm/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 13, High Humidity | Environment | YAKU - Japan | N/A | Payload Alarm | Warning | Ground Cabin %nodelabel% High Humidity | YAKU001/read/45MR-1601-0@DI13-HighHumidit/diStatus | {"value":1} | Payload Alarm: Ground Cabin High Humidity | Payload Alarm: Ground Cabin %nodelabel% High Humidity | Payload Alarm: Ground Cabin %nodelabel% High Humidity&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI13-HighHumidity/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 13, High Humidity | Environment | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% High Humidity | YAKU001/read/45MR-1601-0@DI13-HighHumidit/diStatus | {"value":0} | Payload Alarm: Ground Cabin High Humidity | Payload Alarm: Ground Cabin %nodelabel% High Humidity | Payload Alarm: Ground Cabin %nodelabel% High Humidity&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI13-HighHumidity/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI13-HighHumidity/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 14 AirConditionerStatus | Facilities | YAKU - Japan | N/A | Environmental Alarm | Warning | Ground Cabin %nodelabel% AirConditioner down check site temperature | YAKU001/read/45MR-1601-0@DI14-AirCon/diStatus | {"value":1} | Environmental Alarm: Ground Cabin AirConditioner down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% AirConditioner down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% AirConditioner down check site temperature&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI14-AirCon/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 14 AirConditionerStatus | Facilities | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Cabin %nodelabel% AirConditioner down check site temperature | YAKU001/read/45MR-1601-0@DI14-AirCon/diStatus | {"value":0} | Environmental Alarm: Ground Cabin AirConditioner down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% AirConditioner down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% AirConditioner down check site temperature&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI14-AirCon/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI14-AirCon/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 15. FanTray | Environment | YAKU - Japan | N/A | Environmental Alarm | Warning | Ground Cabin %nodelabel% Fan Cooling System down check site temperature | YAKU001/read/45MR-1601-0@DI15-FanTray/diStatus | {"value":1} | Environmental Alarm: Ground Cabin Fan Cooling System down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% Fan Cooling System down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% Fan Cooling System down check site temperature&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI15-FanTray/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 15. FanTray | Environment | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Cabin %nodelabel% Fan Cooling System down check site temperature | YAKU001/read/45MR-1601-0@DI15-FanTray/diStatus | {"value":0} | Environmental Alarm: Ground Cabin Fan Cooling System down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% Fan Cooling System down check site temperature | Environmental Alarm: Ground Cabin %nodelabel% Fan Cooling System down check site temperature&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI15-FanTray/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI15-FanTray/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Switch | 1, PositionerMisalignment | Payload Antenna | YAKU - Japan | N/A | Payload Alarm | Emergency | Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | YAKU001/read/45MR-1601-1@DI00-PostnrMisalign/diStatus | {"value":1} | Payload Alarm: Ground Cabin SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI00-PositionerMisalignment/diStatus/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Switch | 1, PositionerMisalignment | Payload Antenna | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | YAKU001/read/45MR-1601-1@DI00-PostnrMisalign/diStatus | {"value":0} | Payload Alarm: Ground Cabin SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI00-PositionerMisalignment/diStatus/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/DI00-PositionerMisalignment/diStatus/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Pot | 0, Q-BandRSSI | Payload Ground Station | YAKU - Japan | N/A | Environmental Alarm | NA - to be configured as part of correlation rules | Ground Cabin %nodelabel% Q-BandRSSI obove safe treshold | YAKU001/read/45MR-3800-0@AI0-QBandRSSI/aiValueRaw | {"value":1} | Environmental Alarm: Ground Cabin Q-BandRSSI obove safe treshold | Environmental Alarm: Ground Cabin %nodelabel% Q-BandRSSI obove safe treshold | Environmental Alarm: Ground Cabin %nodelabel% Q-BandRSSI obove safe treshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/AI0-QBandRSSI/aiValueRaw/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Pot | 0, Q-BandRSSI | Payload Ground Station | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Cabin %nodelabel% Q-BandRSSI obove safe treshold | YAKU001/read/45MR-3800-0@AI0-QBandRSSI/aiValueRaw | {"value":0} | Environmental Alarm: Ground Cabin Q-BandRSSI obove safe treshold | Environmental Alarm: Ground Cabin %nodelabel% Q-BandRSSI obove safe treshold | Environmental Alarm: Ground Cabin %nodelabel% Q-BandRSSI obove safe treshold&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/AI0-QBandRSSI/aiValueRaw/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/DigitalInput/AI0-QBandRSSI/aiValueRaw/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Pot | 1, CustomerNodeB-WideBandPower | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | NA - to be configured as part of correlation rules | Ground Cabin %nodelabel% Customer node Band Power - outside normal limits consult Node B operator | YAKU001/read/45MR-3800-0@AI1-NodeBWBandPw/aiValueRaw | {"value":1} | Payload Alarm: Ground Cabin Customer node Band Power - outside normal limits consult Node B operator | Payload Alarm: Ground Cabin %nodelabel% Customer node Band Power - outside normal limits consult Node B operator | Payload Alarm: Ground Cabin %nodelabel% Customer node Band Power - outside normal limits consult Node B operator&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI1-NodeBWBandPower/aiValueRaw/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Pot | 1, CustomerNodeB-WideBandPower | Payload Ground Station | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% Customer node Band Power - outside normal limits consult Node B operator | YAKU001/read/45MR-3800-0@AI1-NodeBWBandPw/aiValueRaw | {"value":0} | Payload Alarm: Ground Cabin Customer node Band Power - outside normal limits consult Node B operator | Payload Alarm: Ground Cabin %nodelabel% Customer node Band Power - outside normal limits consult Node B operator | Payload Alarm: Ground Cabin %nodelabel% Customer node Band Power - outside normal limits consult Node B operator&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI1-NodeBWBandPower/aiValueRaw/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI1-NodeBWBandPower/aiValueRaw/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Pot | 2, PositionerMisalignment | Payload Antenna | YAKU - Japan | N/A | Payload Alarm | Emergency | Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | YAKU001/read/45MR-3800-0@AI2-PostMisalign/aiValueRaw | {"value":1} | Payload Alarm: Ground Cabin SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI2-PostMisalign/aiValueRaw/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Pot | 2, PositionerMisalignment | Payload Antenna | YAKU - Japan | N/A | Payload Alarm | Cleared | Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | YAKU001/read/45MR-3800-0@AI2-PostMisalign/aiValueRaw | {"value":0} | Payload Alarm: Ground Cabin SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment | Payload Alarm: Ground Cabin %nodelabel% SBAND Antena Positioner Misalignment&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Major | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI2-PostMisalign/aiValueRaw/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI2-PostMisalign/aiValueRaw/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Thermo Couple Card | 3, SiteTemperature | Environment | YAKU - Japan | N/A | Environmental Alarm | Warning | Ground Station %nodelabel% Site Temperature above safe levels | YAKU001/read/45MR-6810-0@AI3-SiteTemp/aiValueRaw | {"value":1} | Environmental Alarm: Ground Station Site Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Site Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Site Temperature above safe levels&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI3-SiteTemp/aiValueRaw/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Thermo Couple Card | 3, SiteTemperature | Environment | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Station %nodelabel% Site Temperature above safe levels | YAKU001/read/45MR-6810-0@AI3-SiteTemp/aiValueRaw | {"value":0} | Environmental Alarm: Ground Station Site Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Site Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Site Temperature above safe levels&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI3-SiteTemp/aiValueRaw/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI3-SiteTemp/aiValueRaw/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
Thermo Couple Card | 4, CabinetTemperature | Environment | YAKU - Japan | N/A | Environmental Alarm | Warning | Ground Station %nodelabel% Cabinet Temperature above safe levels | YAKU001/read/45MR-6810-0@AI4-CabTemp/aiValueRaw | {"value":1} | Environmental Alarm: Ground Station Cabinet Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Cabinet Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Cabinet Temperature above safe levels&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI4-CabTemp/aiValueRaw/1 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" auto-clean="false"
Thermo Couple Card | 4, CabinetTemperature | Environment | YAKU - Japan | N/A | Environmental Alarm | Cleared | Ground Station %nodelabel% Cabinet Temperature above safe levels | YAKU001/read/45MR-6810-0@AI4-CabTemp/aiValueRaw | {"value":0} | Environmental Alarm: Ground Station Cabinet Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Cabinet Temperature above safe levels | Environmental Alarm: Ground Station %nodelabel% Cabinet Temperature above safe levels&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Warning | uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI4-CabTemp/aiValueRaw/0 | reduction-key="%uei%:%dpname%:%nodeid%:%parm[message-topic]%" alarm-type="1" clear-key="uei.opennms.org/mqttplugin/altohaps/v1/read/AnalogueInput/AI4-CabTemp/aiValueRaw/1:%dpname%:%nodeid%:%parm[message-topic]%" auto-clean="false"
COMMANDS - WRITE | only used as events
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Power Amp Power Amp RF Disconnect | YAKU001/write/45MR-2404-0@QBandPARF_Discon/relayStatus | {"value":1} | Command: Ground Station Power Amp Power Amp RF Disconnect | Command: Ground Station %nodelabel% Power Amp Power Amp RF Disconnect | Command: Ground Station %nodelabel% Power Amp Power Amp RF Disconnect&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControl/QBandTxPower/relayStatus/1
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Power Amp Power Amp RF Disconnect | YAKU001/write/45MR-2404-0@QBandPARF_Discon/relayStatus | {"value":0} | Command: Ground Station Power Amp Power Amp RF Disconnect | Command: Ground Station %nodelabel% Power Amp Power Amp RF Disconnect | Command: Ground Station %nodelabel% Power Amp Power Amp RF Disconnect&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControl/QBandTxPower/relayStatus/0
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Power Amp has been reset | YAKU001/write/45MR-2404-0@QBandPAReset/relayStatus | {"value":1} | Command: Ground Station Power Amp has been reset | Command: Ground Station %nodelabel% Power Amp has been reset | Command: Ground Station %nodelabel% Power Amp has been reset&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControlQBandPARF_Discon/relayStatus/1
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Power Amp has been reset | YAKU001/write/45MR-2404-0@QBandPAReset/relayStatus | {"value":0} | Command: Ground Station Power Amp has been reset | Command: Ground Station %nodelabel% Power Amp has been reset | Command: Ground Station %nodelabel% Power Amp has been reset&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControlQBandPARF_Discon/relayStatus/0
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Site Firewall has been rebooted | YAKU001/write/45MR-2404-0@SiteFWReboot/relayStatus | {"value":1} | Command: Ground Station Site Firewall has been rebooted | Command: Ground Station %nodelabel% Site Firewall has been rebooted | Command: Ground Station %nodelabel% Site Firewall has been rebooted&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControl/SiteFWReboot/relayStatus/1
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Site Firewall has been rebooted | YAKU001/write/45MR-2404-0@SiteFWReboot/relayStatus | {"value":0} | Command: Ground Station Site Firewall has been rebooted | Command: Ground Station %nodelabel% Site Firewall has been rebooted | Command: Ground Station %nodelabel% Site Firewall has been rebooted&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControl/SiteFWReboot/relayStatus/0
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Door Status open when relayStaturs = 1 | YAKU001/write/45MR-2404-0@Door/relayStatus | {"value":1} | Command: Ground Station Door Status open when relayStaturs = 1 | Command: Ground Station %nodelabel% Door Status open when relayStaturs = 1 | Command: Ground Station %nodelabel% Door Status open when relayStaturs = 1&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControl/Door/relayStatus/1
YAKU001 | 45MR-2404-01 |  | YAKU - Japan |  | Command | Normal | Ground Station %nodelabel% Door Closed when relayStatus = 0 | YAKU001/write/45MR-2404-0@Door/relayStatus | {"value":0} | Command: Ground Station Door Closed when relayStatus = 0 | Command: Ground Station %nodelabel% Door Closed when relayStatus = 0 | Command: Ground Station %nodelabel% Door Closed when relayStatus = 0&lt;BR&gt;mqtt plugin received message from topic %parm[message-topic]&lt;BR&gt; all message parameters: %parm[all]% | Normal | uei.opennms.org/mqttplugin/altohaps/v1/write/RemoteControl/Door/relayStatus/0

## input
Alarms
Mimic Component | RTU Alarm Name | Alarm Category | Hidden Alarm detials from NOC staff Default Moxa Topic - broker | Open NMS UEI | Noc Staff Log user message | Description | Location | Relay Status | Event Type | Severity
Switch | 0, MainsPowerStatus | Mains Power | YAKU001/read/45MR-1601-0@DI00-GSMains/diStatus | YAKU001/read/DigitalInput/DI00-GSMains/diStatus | Ground Cabin Station YAKU001 Mains Power Failed | Ground Cabin Station YAKU001 Mains Power Failed | YAKU - Japan | N/A | EnvironmentalAlarm | Emergency
Switch | 1, UPS Down | UPS Power | YAKU001/read/45MR-1601-0@DI01-UPS/diStatus | YAKU001/read/DigitalInput/DI01-UPS/diStatus | UPS Down no backup power supply | UPS Down no backup power supply | YAKU - Japan | N/A | EnvironmentalAlarm | Alert
Switch | 2, QBandPSU | Qband PowerSupply | YAKU001/read/45MR-1601-0@DI02-QBandPSU/diStatus | YAKU001/read/DigitalInput/DI02-QBandPSU/diStatus | Ground Cabin Station YAKU001 Qband Power Supply Unit Failed | Ground Cabin Station YAKU001 Qband Power Supply Unit Failed | YAKU - Japan | N/A | Payload Alarm | Emergency
Switch | 3, Q_band_PA_Status | Payload Ground Station | YAKU001/read/45MR-1601-0@DI03-QBandPA_Off/diStatus | YAKU001/read/DigitalInput/DI03-QBandPA_off/diStatus | Ground Cabin Station YAKU001 QBand Power Amp Failed | Ground Cabin Station YAKU001 QBand Power Amp Failed | YAKU - Japan | N/A | Payload Alarm | Emergency
Switch | 4, RF_input_over_ limit | Payload Ground Station | YAKU001/read/45MR-1601-0@DI04-QBandRFOvrL/diStatus | YAKU001/read/DigitalInput/DI04-QBandRFOverLimit/diStatus | Ground Cabin Station YAKU001 Qband Radio Frequency Over Limit | Ground Cabin Station YAKU001 Qband Radio Frequency Over Limit | YAKU - Japan | N/A | Payload Alarm | Critical
Switch | 5, QBandOverCurrent | Payload Ground Station | YAKU001/read/45MR-1601-0@DI05-QBandOverCu/diStatus | YAKU001/read/DigitalInput/DI05-QBandOverCurrent/diStatus | Ground Cabin Station YAKU001 Qband OverCurrent above safe threshold | Ground Cabin Station YAKU001 Qband OverCurrent above safe threshold | YAKU - Japan | N/A | Payload Alarm | Alert
Switch | 6, QBandOverTemperature | Payload Ground Station | YAKU001/read/45MR-1601-0@DI06-QBandOverTm/diStatus | YAKU001/read/DigitalInput/DI06-QBandOverTemp/diStatus | Ground Cabin Station YAKU001 Qband Temperature above safe threshold | Ground Cabin Station YAKU001 Qband Temperature above safe threshold | YAKU - Japan | N/A | Payload Alarm | Alert
Switch | 7, PositionerControllerStatus [ python app on Intel NUC propering FMS web service at sampling intervals if the plane is in service to confirm that Positioner is aligned with Aircraft] | Payload Antenna | YAKU001/read/45MR-1601-0@DI07-PosCtrlFail/diStatus | YAKU001/read/DigitalInput/DI07-PosCtrlFail/diStatus | Ground Cabin Station YAKU001 S-Band Ground Station YAKU001 Antena Positioner Failed | Ground Cabin Station YAKU001 S-Band Ground Station YAKU001 Antena Positioner Failed | YAKU - Japan | N/A | Payload Alarm | Emergency
Switch | 8, VSWRHigh | Payload Ground Station | YAKU001/read/45MR-1601-0@DI08-VSWHigh/diStatus | YAKU001/read/DigitalInput/DI08-VSWHigh/diStatus | Ground Cabin Station YAKU001 VSWHigh above safe threshold | Ground Cabin Station YAKU001 VSWHigh above safe threshold | YAKU - Japan | N/A | Payload Alarm | Alert
Switch | 9, Bay1DoorStatus | Facilities | YAKU001/read/45MR-1601-0@DI09-BayDoorStat/diStatus | YAKU001/read/DigitalInput/DI09-BayDoorStatus/diStatus | Ground Cabin Station YAKU001 BayDoor Open | Ground Cabin Station YAKU001 BayDoor Open | YAKU - Japan | N/A | Security | Warning
Switch | 10, Antenna PSU | Facilities | YAKU001/read/45MR-1601-0@DI10-AntennaPSU/diStatus | YAKU001/read/DigitalInput/DI10-AntennaPSU/diStatus | Ground Cabin Station YAKU001 SiteMonitor Down | Ground Cabin Station YAKU001 SiteMonitor Down | YAKU - Japan | N/A | Security | Emergency
Switch | 11, High Cabinet Temp | Facilities | YAKU001/read/45MR-1601-0@DI11-HighCapTemp/diStatus | YAKU001/read/DigitalInput/DI11-HighCapTemp/diStatus | Ground Cabin Station YAKU001 High Cabinet Temperature | Ground Cabin Station YAKU001 High Cabiner Temperature | YAKU - Japan | N/A | Security | Critical
Switch | 12, Smoke Alarm | Environment | YAKU001/read/45MR-1601-0@DI12-SmokeAlarm/diStatus | YAKU001/read/DigitalInput/DI12-SmokeAlarm/diStatus | Ground Cabin Station YAKU001 Smoke Alarm triggered on | Ground Cabin Station YAKU001 SmokeAlarm triggered on | YAKU - Japan | N/A | Payload Alarm | Warning
Switch | 13, High Humidity | Environment | YAKU001/read/45MR-1601-0@DI13-HighHumidit/diStatus | YAKU001/read/DigitalInput/DI13-HighHumidity/diStatus | Ground Cabin YAKU001 High Humidity | Ground Cabin YAKU001 High Humidity | YAKU - Japan | N/A | Payload Alarm | Warning
Switch | 14 AirConditionerStatus | Facilities | YAKU001/read/45MR-1601-0@DI14-AirCon/diStatus | YAKU001/read/DigitalInput/DI14-AirCon/diStatus | Ground Cabin Station YAKU001 AirConditioner down check site temperature | Ground Cabin Station YAKU001 AirConditioner Down check site temperature | YAKU - Japan | N/A | EnvironmentalAlarm | Warning
Switch | 15. FanTray | Environment | YAKU001/read/45MR-1601-0@DI15-FanTray/diStatus | YAKU001/read/DigitalInput/DI15-FanTray/diStatus | Ground Cabin Station YAKU001 Fan Cooling System down check site temperature | Ground Cabin Station YAKU001 Fan Cooling System down check site temperature | YAKU - Japan | N/A | EnvironmentalAlarm | Warning
Switch | 1, PositionerMisalignment | Payload Antenna | YAKU001/read/45MR-1601-1@DI00-PostnrMisalign/diStatus | YAKU001/read/DigitalInput/DI00-PositionerMisalignment/diStatus | Ground Cabin Station YAKU001 SBAND Antena Positioner Misalignment | Ground Cabin Station YAKU001 SBAND Antena Positioner Misalignment | YAKU - Japan | N/A | Payload Alarm | Emergency
Pot | 0, Q-BandRSSI | Payload Ground Station | YAKU001/read/45MR-3800-0@AI0-QBandRSSI/aiValueRaw | YAKU001/read/DigitalInput/AI0-QBandRSSI/aiValueRaw | Ground Cabin Station YAKU001 Q-BandRSSI obove safe treshold | Ground Cabin Station YAKU001 Q-BandRSSI obove safe treshold | YAKU - Japan | N/A | EnvironmentalAlarm | NA - to be configured as part of correlation rules
Pot | 1, CustomerNodeB-WideBandPower | Payload Ground Station | YAKU001/read/45MR-3800-0@AI1-NodeBWBandPw/aiValueRaw | YAKU001/read/AnalogueInput/AI1-NodeBWBandPower/aiValueRaw | YAKU Customer node Band Power - outside normal limits consult Node B operator | YAKU Customer node Band Power - outside normal limits consult Node B operator | YAKU - Japan | N/A | Payload Alarm | NA - to be configured as part of correlation rules
Pot | 2, PositionerMisalignment | Payload Antenna | YAKU001/read/45MR-3800-0@AI2-PostMisalign/aiValueRaw | YAKU001/read/AnalogueInput/AI2-PostMisalign/aiValueRaw | Ground Cabin Station YAKU001 SBAND Antena Positioner Misalignment | Ground Cabin Station YAKU001 SBAND Antena Positioner Misalignment | YAKU - Japan | N/A | Payload Alarm | Emergency
Thermo Couple Card | 3, SiteTemperature | Environment | YAKU001/read/45MR-6810-0@AI3-SiteTemp/aiValueRaw | YAKU001/read/AnalogueInput/AI3-SiteTemp/aiValueRaw | Ground Station YAKU001 Site Temperature above safe levels | Ground Cabin Station YAKU001 Site Temperature above safe levels | YAKU - Japan | N/A | EnvironmentalAlarm | Warning
Thermo Couple Card | 4, CabinetTemperature | Environment | YAKU001/read/45MR-6810-0@AI4-CabTemp/aiValueRaw | YAKU001/read/AnalogueInput/AI4-CabTemp/aiValueRaw | Ground Station YAKU001 Cabinet Temperature above safe levels | Ground Cabin Station YAKU001 Site Temperature above safe levels | YAKU - Japan | N/A | EnvironmentalAlarm | Warning
Commands
YAKU001 | 45MR-2404-01 |  | YAKU001/write/45MR-2404-0@QBandPARF_Discon/relayStatus | YAKU001/write/RemoteControl/QBandTxPower/relayStatus | Power Amp Power Amp RF Disconnect |  | YAKU - Japan
YAKU001 | 45MR-2404-01 |  | YAKU001/write/45MR-2404-0@QBandPAReset/relayStatus | YAKU001/write/RemoteControlQBandPARF_Discon/relayStatus | Power Amp has been reset |  | YAKU - Japan
YAKU001 | 45MR-2404-01 |  | YAKU001/write/45MR-2404-0@SiteFWReboot/relayStatus | YAKU001/write/RemoteControl/SiteFWReboot/relayStatus | Site Firewall has been rebooted |  | YAKU - Japan
YAKU001 | 45MR-2404-01 |  | YAKU001/write/45MR-2404-0@Door/relayStatus | YAKU001/write/RemoteControl/Door/relayStatus | Door Status open when relayStaturs = 1 |  | YAKU - Japan
YAKU001 | 45MR-2404-01 |  | YAKU001/write/45MR-2404-0@Door/relayStatus | YAKU001/write/RemoteControl/Door/relayStatus | Door Closed when relayStatus = 0 |  | YAKU - Japan